SECTION 26 52 00

EMERGENCY LIGHTING

Page 1 of 3

REV 13.2.1

PART 1 GENERAL

  - SECTION INCLUDES

- Central Battery Systems

  - REFERENCES

- NFPA 101- Life Safety Code

- NFPA 70 – National Electrical Code

- UL 924 – Standards for Emergency Lighting & Power Equipment

  - SUBMITTALS

- Shop Drawings: Indicate dimensions and components for each physical component, in addition to wiring diagram for any “system” to be provided under this contract.

- Product Data: Provide dimensions, ratings and performance data.

- Submit manufacturer’s installation instructions. Indicate application conditions and limitations of use stipulated by product testing agency specified under Regulatory Requirements. Include instructions for storage, handling, protection, examination, preparation and installation of product.

- Submit manufacturer’s operation and maintenance instructions for each product.

  - QUALIFICATIONS

- Manufacturer: Company specializing in manufacturing the emergency lighting products specified in this section with minimum five years experience.

  - REGULATORY REQUIREMENTS

- Conform to requirements of NFPA 101 and NFPA 70.

- Products: Listed and labeled as required by Underwriter’s Laboratories Standard for Safety UL 924, Emergency Lighting and Power Equipment, as suitable for the purpose specified and indicated.

REV13.2.1

PART 2: PRODUCTS

  - CENTRAL BATTERY SYSTEMS

- Manufacturers

  - Signtex Lighting, Inc: Series CBS

  - Engineer Approved Equals

- System Description

  - Signtex Series CBS Central Battery System shall provide control and battery backup power for a minimum of 90 minutes to all emergency fixtures connected to the system, including exit signs, emergency lights, and night lights. As an option, all fixtures may operate in normal ON mode (when building power is available) in addition to emergency operation. All fixtures operate at 24VDC in both emergency and normal ON operation.

- Construction and Operation

  - The power supply is to be a UPS system per NEC 700.12 (c) with storage batteries, charging system, automatic transfer switch and self-test switch with an LED indicator, providing uninterrupted output at 24VDC for loads as specified for at least 90 minutes in emergency operation. The Push to Test Switch and Diagnostic Status Indicator allow immediate update on battery condition and charger performance.

  - The system shall include automatic self testing/self-diagnostic system as required by NFPA 101 (2009) Section 7.9.3, Periodic Testing of Emergency Lighting Equipment. Per NFPA 101 Section 7.9.3.1.2, failure of components as defined in UL Standard 924 shall be indicated by means of the LED status indicator.

  - The battery and charger system enclosure shall be a NEMA Type 1, UL 50 steel cabinet, for surface or optional recessed mount.

  - Maintenance on the batteries or other electronics for all emergency lighting equipment on one building floor can be performed without requiring access to the lighting fixtures, except for lamp failures.

  - Maximum charge time shall be 72 hours.

  - The DC wiring output terminals in each CBS system shall have up to 8 circuits available for lighting devices.

REV 13.2.1

- Fixtures, Installation and Wiring

  - Refer to Lighting Fixture Schedule on plans for details. All fixtures shall be equipped with LED lamps, except for Series CVRE recessed emergency light with MR16 incandescent lamps.

  - Emergency lighting fixtures may include, but are not limited to: Signtex MOONLITE  Series MLD (Recessed Downlight), Series MLW (Wall Mount), Series MOE (Exterior Wall Mount), Series MLS (Surface Mount Downlight), Series MUE (Exterior Mullion Mount), Series MAE (Exterior Wall Mount, Series MFP (Recessed Wall Mount Exterior Floor Proximity), Series MHE (Exterior/Interior Surface or Recessed Mount High Bay), or Series CVRE (Recessed light with moving doors). Exit signs may include Signtex Series RPR (Die Cast exit signs), Series CRS or CRR (Edge Lit exit signs), Series BLD (Thermoplastic Housing exit signs), or Series BLW (Die Cast Wet Location Exit signs).

  - Branch circuits shall be wired with conductor sizes from #12 to #8 AWG. Flexible metal case (Type MC Class 1) cable is recommended for most applications, however provided applicable current limits are met, Class 2 (low voltage/current limited) wiring may be installed. Verify any specifications for wiring required by local codes.

  - The number of conductors required in any branch circuit shall be from 2 to 4, as required by the type of fixture and operation specifications. See Signtex Installation and Instruction Manuals for detailed requirements.

  - Verify maximum run lengths meet manufacturer’s recommendations for voltage drop at the given load, per NEC 700.9.

  - In accessible ceiling areas, low voltage emergency power cabling can be installed on J-hooks or other similar means designed for use above accessible ceilings.

  - In exposed or non-accessible ceilings, emergency power cabling shall be installed in conduit.